## job1
|  | * SCHEDULE OF QUANTITY * |  |  | Estimated cost:- | Rs. | 647290
| Name of work:- | Construction of flow irrigation scheme Garuhl kuhl in Gram Panchayat Banuri, Holta, Banuri khas, Moli Chak and Band Vihar in Tehsil Palampur District Kangra(HP). |  |  | Earnest money:- | Rs. | 17210
|  | (SH)Construction of reinforcement cement concrete channel from RD 3340 to 3640 running metre = 300 running metre. |  |  | Time :- | Six months
Sr. | Description of items. |  | Qty. | Rate in |  |  | Unit | Amount.
No. |  |  |  | Figure | Words.
1 | Excavation in drain and channels etc. in all kinds of soil such as pick work,jumper work,blasting work soft and hard rock and saturated soil including dressing of sides and beds and disposing of excavated earth upto a lead of 20 metre and lift upto 1.50 metre within all leads and lifts as per the direction of Engineer-in-charge. |  | 79.2 |  |  |  | Per
|  |  | cubic |  |  |  | cubic
|  |  | metre |  |  |  | metre
2 | Providing and laying cement concrete 1:4:8 (One cement is to four sand is to eight graded stone aggregate 40 milimetre nominal size) and curing complete excluding the cost of form work in foundation and plinth with in all leads and lifts as per the direction of Engineer-in-charge. |  | 20.25 |  |  |  | Per
|  |  | cubic |  |  |  | cubic
|  |  | metre. |  |  |  | metre
3 | Providing and laying cement concrete 1:2:4 (One cement is to two sand is to four graded stone aggregate 20 milimetre nominal size) and curing complete excluding the cost of form work and reinforcement for reinforced cement concrete in:-
(a) | Foundation,footings bases of column and the like mass concrete within all leads and lifts as per the direction of Engineer-in-charge. |  | 30 |  |  |  | Per cubic metre
cubic
metre
(b) | Walls (any thickness) butt not less then 0.10 metre thickness) attached pillasters, buttresses, plinth and string courses etc. from top of foundation up to floor two level with in all leads and lifts as per the direction of Engineer-in-charge. |  | 37.5 |  |  |  | Per cubic metre
cubic
metre
4 | Providing form work with steel plates 3.15 milimetre thick welded with angle iron in frame 30*30*5 milimetre so as to give a fair finish including centring,shuttering,strutting and propping etc. with wooden battens ballies,height of propping and centring below supporting floor two ceiling not exceeding 4 metre and removal of the same for in-situ-reinforced concrete and plain concrete work in-
a) | Vertical surfaces such as walls(any thickness)partitions walls and the like including attached pillasters,buttreses plinth string courses and the like within all leads and lifts as per the direction of Engineer-in-charge |  | 675 |  |  |  | Per
|  |  | square |  |  |  | square
|  |  | metre |  |  |  | metre
5 | Providing and laying mild steel/tor steel reinforcement for reinforced cement concrete work including bending binding and placing in position complete upto floor two level within all leads and lifts as per the direction of Engineer-in-charge. |  | 2700 |  |  |  | Per Killo-gramme
Killo-
gramme.
6 | Providing & laying P.V.C. water stop seal 230x6 mm thick 20 metre center to center of expension cum construction joint within all leads and lifts as per the direction of Engineer-in-charge. |  | 21 |  |  |  | Per
|  |  | running |  |  |  | running
|  |  | metre |  |  |  | metre
Terms and conditions:-
a) | Cement will be issued @ Rs.303/-per bag from Departmental Divisional store Differpat.
b) | Steel will be issued @ Rs.4800/-per quintal to the contractor from Divisional store.
c) | Crushed stone aggregate and mechanically mixture concrete shall be used. | Nothing shall be paid for the rejected work.
d) | The work shall be completed with in stipulated period.
e) | Required No. of test cubes of cement concrete 1:2:4 (1 cement:2 sand:4 graded stone agg. of 20 mm nominal size) from site shall be collected for random testing of their compressive strength at 28 days as per provision of BIS 456-2000 which shall be get tested from the lab of HPPWD of NIT Hamirpur.
f) | Conditional and telegraphy tender are liable to be rejected.
g) | All pages of the tender from must be signed before submitting the tender falling which the tender is liable to be treated as invalid.
h) | The work shall be executed as per IPH/HPWD specification and relevant IS codes to the entire satisfaction of the Engineer-in-Charge.
i) | The security, income tax, GST and surcharge and labour welfare cess if any shall deducted from each running bill of the contractor/firm as applicable.
j) | All necessary documents such as income tax clearance certificate, renewal of registration, CST/GST nos shall have to be produced by the contractor/firm before purchase of tender documents.
k) | The offer shall be valid fore 120 days from the date of the opening of the tender.
l) | The rate of all item should be inclusive of all taxes, duties, levies, carriage of material within all leads and lifts etc. to site of work.
m) | Any damages caused to any public and private property during the course of execution of work shall be restored by the contrctor and if, not done within a reasonable time then the same shall be restored by the Department at contractors cost.
n) | Nothing shall be paid for the rejected work/material.
o) | The contractor shall be fully responsible for watch and ward of material at the site of work.

## job2
|  | * SCHEDULE OF QUANTITY * |  |  |  |  | Estimated cost:- | Rs. | 189803
| Name of work:- | Providing lift water supply scheme to PC habitation of census village Chudrehar and Molichak in gram panchayat Molichak in Tehsil Palampur District Kangra(HP). |  |  |  |  | Earnest money:- | Rs. | 3800
|  | (SH)Supply and errection of pumping machinery alongwith allied accessories for tube well and laying, jointing & testing of rising main 125 milimetre dia galvainsed iron pipe (Medium class). |  |  |  |  | Time :- | Six months
Sr. No. | Description of items. |  |  |  | Quantity | Rate in |  |  | Unit | Amount.
[6 empty] | Figure | Words.
1 | Supply of Submersible clear cold & fresh water pumping sets of reputed make such as KSB/B/s/Oswal/Calama/wrothington with bronze impeller conforming to latest relevant BIS code.The pump should be fitted with closed bronze impellers as per IS:8034-1976 latest suitable for clear cold water having greased packed bearings and shaft with wound stator on motor side and with shaft protection sleave on pump side ensuring better life for shaft conforming to BIS specifications. The pump shall be directly coupled to a submersible squirrel cage induction motor of kirlosikar/NGEF/Jyoti/Crompton make conforming to BIS 9285-1979 latest with upto date amendments. Totally dust and water proof for submersible duly isolated from the pump by intermediate casing with double mechanical seal in oil chamber and grease packed lubricated bearings and provided with stainless steel thrust bearings plate to withstanding vertical loads with minimum wear and tear. It should also be fitted with a device to take up expansion of water with the heating of motor. The pump set should include water level guards errection clamps,cable clips and depth gauge etc.and and suitable for operation on data given below :- |  |  |  | 1 x 15=15 |  |  |  | Per
[5 empty] | horse power. |  |  |  | horse
power
A) | SITE CONDITIONS :-
i) | Location of site | The site is located at a distance 12 KM from Palampur.
ii) | The altitude of place in which pumping set is intended to work in ordinary service if it exceeds 1000 mt. | Altitude of place is 900 metre above MSL
iii) | Humidity | Whether generally remains humid during Monsoon Season.
iv) | Nature of autmosphere | As normally encountered in Shivalik range .
v) | Detail of quility of wate | Clear water from Tube well
vi) | Water free from sand or not | Free from sand
vii) | Water corosive or not | Not Corosive
viii) | Turbidity if any | <50 PPM
ix) | Type of well | Tube well
x) | Size of well
xi) | Depth of water during HFL in the Pond. | metres.
xii) | Maximum draw down. | 35.73 metres.
xiii) | Depth of well | 64metres.
xiv) | Any other information or requirement | _____ metres.
B) | OPERATING CONDITIONS :-
i) | Type of current | AC three / single phase.
ii) | Operation frequency | 50 HZ
iii) | Rated Voltage | 400 ( +/- ) 10% volts.
iv) | System of earthing if any to be adopted. | Double loop earthing as per BIS-3043-1987 Latst With upto date ammendments.
v) | Speed of revolution in RPM | To be quoted by the tenderer
vi) | Direction of rotation | To be quoted by the tenderer
vii) | No of working hours per day. | 8 hours.
viii) | The Max. Temp. of cooling air and water in the place in which the motor set is intended to work in ordinary service. | 35 degree centigrade.
C) | MOTOR
i) | Ref. to BIS code | BIS-9283-1979 with BIS 900-1992 up to date ammendments.
ii) | Type of enclosure of motor | SPD (As per BIS - 4691- 1985 (latest)
iii) | Type of duty. | Contineous.
iv) | Mechanical output in K.W. | Suitable for driving submersible pumps, required for duties specified against pump to avoid overloading of motor a margin of about 15 - 20 % may be kept in the rated output of prime mover.
D) | PUMP
a) | No of pumps required. | 1 Number pump
b) | Spare parts required | For two years normal maintenance as recommended by manufacturer.
c) | Type of drive | Electric induction motor
d) | Optional fittings reqd. | ~~~~
e) | Class of insulation- | Class B
f) | Max. permissible temp.rise of motor reqd.is different from that given in B (viii) above. | To be specified by the tendrer
g) | Particulars of test reqd. & where they are to be conducted | As per terms and conditions
h) | Particulars as to whether voltage limiting device will be employed | Star delta starter Oil immersed fully automatic to be installed between bus bar and motor shunt capacitor is also proposed to be installed for improving the power factor at site.
NOTE :-Star delta starter upto 37.5KW & ATS for 37.5Kw to 50Kw.Staror rotor starter with slipering motor beyond 50Kw.
ix) | Type of Motor | As per BIS 9283-1979 or latest
x) | Details of shaft extension required | To work with the pump offered.
xi) | Breakway torque in terms of rated load torque & the corresponding breakway starting current which may be taken from the supply with the starting apparatus in circuit. | Breakway torque to be given by the tenderer but the starting current should not exceed 2.5 times of the full load current.
xii) | Nature of load & any information regarding the driven machine which has a bearing up on the torque required during the accelerated period, the kinetic energy of the moving parts to be accelerated and No. of starts during a specified period. | To work the Pump offered.
xiii) | Where possible fault capacity of the system to which the motor is connected | The motor should be able to with stand initial current for 2.5 times the rated currents for two minutes without suffering damages or permanent deformations.
E) | PUMP OPERATING CONDITIONS :-
i) | Capacity | 10 LPS for each pump
ii) | Total head in metres | 59.482 Meters
If total head is not known then following details be provided
a) | Static Head | 56.04 Metres
b) | Minimum depth of water | 64.50 Metres.
c) | Variation in water level | Metres
d) | Ground level to Maximum water level | 1824.20 Metres
e) | Ground level to delivery points | 1883.53 Metres
f) | Pressure in the suction tank | ~ Kg/cm2
g) | Pressure in the delivery tank | ~ Kg/cm2
iii) | Length of Rising main | 90 Metre including column assembly
iv) | Dia of Rising main | 80 mm dia G.I.pipe
v) | Drive arrangement | <50 PPM
vi) | Drive type | Electric driven.
vi) | NPSH reqd. | To be quoted by the tenderer
vii) | Limites of total head in which the pump is required to operate. | (-) 15% to ( + ) 10% of total head.
viii) | Suction / delivery size of pump | To be specified by the tendrer.
ix) | Efficiency of pump at | To be specified by the tendrer.
x) | Discharge level of highest point. | 1827.15 metre
a) | Duty Head.
b) | ( + ) 10% Head
c) | ( - ) 25% Head.
x) | Material of construction | To be specified by the tendrer (Manufacturers certificate to be appended.) margin of about 15-20% may be kept in the rated out put of prime mover.
2 | Installation of L&T make automatic panel for required horse power including auto start, auto stop and restart facility including single phase preventer, timer, relay, ametre, voltametre, selector switch, hours run metre, prevention of phase reversal, imbalance and dry connector overload and fixed with compatible starter including all allied accessories complete in all respect with in all lead and lift as per satisfaction of Engineer- in-charge. |  |  |  | 1 |  |  |  | Each
Number
3 | Providing M.S sheet 16 SWG steel fabricated floor mounted closed almirah type switch board including angle iron post of suitable height & size ISA 40 X40 X6 mm, duly painted comprising and capable of mounting the following accessories with all internal electric connections. The drawing of panel board shall be subject to approval of the Engineer-in-Charge. |  |  |  | 1 |  |  |  | Each
Number
a) | Three phases indicator lamps complete with toggle switches for individual motors conforming to BIS 3452 part I&II latest with up to date amendments. | 1 No. | each |  | 1 |  |  |  | Each
set
b) | Earth leakage circuit breaker/MCB of recommended make (Kilburn/L&T/MEI/GEC) as per IS:2516-1977 with upto date ammendments and of suitable range with which should have control box, operating handle and trip/reset bush button on/off indicators, re-indicating off spring condition of the circuit breaker for over current protection. The circuit should be equipped with magnet thermal release with metallic tape CTS. It should also be fitted with earth fault for tripping of breaker on occurrence of earth fault on off breaker load side. |  |  |  | 1 |  |  |  | Each
Number
Supply of Kirlosker/Kilburn//IVC/Fources/Gled/BHEL/Leader mak C.I double flanged swing check type reflex valve (class PN-I) having bye pass arrangement and size equal to dia of of Rising main i.e.125mm and shall be suitable for withstanding nominal seat pressure 10 kg/cm2.
4 (a) | Supply of Kirloskar/Kilburn/ IVC/Fouress/Gled/BHEL/Leader make of suitable size cast iron double flanged sluice valve having size of 125 mm dia Class PN-1 equal to delivery of pump and capable of withstanding nominal seat pressure of 16kg/cm2 as per BIS-780-1984 (Latest additation). |  |  |  | 2 |  |  |  | Each
Number
NOTE:- The cast iron Sluice valve shall conform to BIS-780-1984 for 50 mm to 300 mm dia and BIS:2906-1984 for 350 mm to 1200 mm dia (latest eddition). However if seat pressure exceeds the limits prescribed in above mentioned BIS then it shall be of cast steel conforming to class ASA-150 for seat pressure up to 21 Kg./Cm2 & of class ASA-300 for seat pressure 52 Kg./Cm2 as per BS-1414 (API-600).
b) | Supply of Kirloskar/Kilburn/ IVC/Fouress/Gled/BHEL/Leader/ of suitable size cast iron double flanged swing check type reflux valve having bye pass arrangement and size of 125 mm dia class PN-1 equal to delivery of pump for withstanding nominal seat pressure of 16 kg/cm2 As per BIS - 5312-1984 ( part -1) latest with up to date ammendments. |  |  |  | 2 |  |  |  | Each
Number
Supply of Kirlosker/Kilburn//IVC/Fources/Gled/BHEL/Leader mak C.I double flanged swing check type reflex valve (class PN-I) having bye pass arrangement and size equal to dia of of Rising main i.e.125mm and shall be suitable for withstanding nominal seat pressure 10 kg/cm2.
NOTE:- The reflux valve shall conform to BIS-5312-1984 (part-I) latest with upt date ammendments. However if seat pressure exceeds the limits prescribed in BIS 5312 then the reflux valves shall be of cast steel conformingt to class ASA-150 for seat pressure up to 21 Kg./Cm2 & of class ASA-300 for seat pressure 52 Kg./Cm2 as per BS-1414 (API-600).
c) | Supply of Kirloskar/Kilburn/ IVC/Fouress/Gled/BHEL/Leader/ of suitable size cast iron double flanged swing check type reflux valve 80 mm dia having bye pass arrangement class PN-1 equal to rising main for withstanding nominal seat pressure of 16 kg/cm2 As per BIS - 1414 API-600 latest with up to date ammendments. |  |  |  | 1 |  |  |  | Each
Number
NOTE:- The reflux valve shall conform to BIS-5312-1984 (part-I) latest with upt date ammendments. However if seat pressure exceeds the limits prescribed in BIS 5312 then the reflux valves shall be of cast steel conformingt to class ASA-150 for seat pressure up to 21 Kg./Cm2 & of class ASA-300 for seat pressure 52 Kg./Cm2 as per BS-1414 (API-600).
5 (a) | Providing & laying suitable size copper PVC insulated armoured power 2.5 core cable conforming to BIS: 1554(P-1)1988 or latest with upto date ammendments of Siemens Gloster /ICC make from meter of HPSEB to OCB & from OCB to busbar switch & starter ( one cable carrying all three phases ) including all other electrical equipment accessories such as thimbles, flexible, pipes, solder,nuts & bolts, cable glands etc. laid in pipes or tranches under floor.The type size & Make will be subject to approval of HPSEB authorities. In case of non acceptancy by HPSEB authorities it shall have to be replaced by the tenderer free of cost | 5 (a) | Providing and laying PVC insulated jointless,flat water proof copper cable of Siemens/Finolex/Grandla/Gloster make conforming to BIS: 1554 (Part-I)-1988 or latest with upto date ammendments of suitable size for the pump sets offered(One cable carrying all three phases) including all other electrical equipment/accessories such as thimble,flexible pipe solder,nuts & bolts cable gland etc. laid in pipe or trenches under floor . The type size & make will be subject to approval of HPSEB authorities. In case of non acceptance by HPSEB authorities, it shall have to be replaced by the tenderer free of cost. | 5 (a)
| a. On supply side of 2.5 core (from HPSEB meter to switch & starter) = of size 2.5mm2 |  | a. On supply sode of 31/2 core (from HPSEB meter to switch & starte)=10mtr.of size mm2 |  | 10 |  |  |  | Per
[5 empty] | metre |  |  |  | metre
(b) | Providing & laying jointless flat water proof cable as per BIS 694-1990 (latest with upto date ammendments) suitable for the pump set offered from OCB to motor, motor to starter including all other electrical equipments such as Thimbles, flexible pipes, solder, nuts & bolts cable glands etc. laid in pipes or trenches. The type, size & make will be subject to approval of HPSEB authorities. In case of non acceptance by HPSEB authorities it shall have to bhe repalace by the tenderer free of cost. | 5 (a) | Providing and laying PVC insulated jointless,flat water proof copper cable of Siemens/Finolex/Grandla/Gloster make conforming to BIS: 1554 (Part-I)-1988 or latest with upto date ammendments of suitable size for the pump sets offered(One cable carrying all three phases) including all other electrical equipment/accessories such as thimble,flexible pipe solder,nuts & bolts cable gland etc. laid in pipe or trenches under floor . The type size & make will be subject to approval of HPSEB authorities. In case of non acceptance by HPSEB authorities, it shall have to be replaced by the tenderer free of cost. | 5 (a)
| a. On motor side 2.5core (From switch and starter to motor_ = 50 metre of size 2.5mm2 |  | a. On supply sode of 31/2 core (from HPSEB meter to switch & starte)=10mtr.of size mm2 |  | 50 |  |  |  | Per
[5 empty] | metre |  |  |  | metre
c) | Providing and laying double loop earthinmg with copper plate 600x600x3mm thick electrode complete with material such as charcoal,common salt,G.I.pipes.thimbles,nuts & bolts,digging of pits,GI wiring & 25x5mm copper strips required capacity conforming to BIS 3043-1987 latest with upto date ammendments for above motor & other electrical equipments complete in all respect. | b | P/L double loop earthinmg with copper plate 600x600x3mm thick electrical complete with material such as charcoal,common salt,G.I.pipes.thimbles,nuts & bolts,digging of pits,GI wiring & 25x5mm copper strips required capacity conforming to BIS 3043-1987 latest with upto date ammendments for above motor & other electrical equipments. | b | 1 |  |  |  | Each
job
6 | Supply & errection of floor / wall mounted power factor Shunt Capacitor conforming to BIS 2834-1986 latest with up to date ammendments BHEL,GEC,Machneil/Bajaj make to raise the prevailing power factor at site to 0.95 for direct connection to induction motor individually, of required KVAR according to HP of motor offered including cable Siemens/Gloster/ICC make from busbar chamber to capacitor and also including LT/ LK/ Kilburn make ICTP switches conforming to BIS 4064-1978 or latest with HRC fuses ( Range to be specified by the tenderer.) |  |  |  | 1 x 4 |  |  |  | Per
[5 empty] | = 4 KVAR |  |  |  | KVAR
Supply of Kirlosker/Kilburn//IVC/Fources/Gled/BHEL/Leader mak C.I double flanged swing check type reflex valve (class PN-I) having bye pass arrangement and size equal to dia of of Rising main i.e.125mm and shall be suitable for withstanding nominal seat pressure 10 kg/cm2.
7 | Providing and laying delivery pipe considering site requirement, NPSH required & available & common header having area equle to two times the area of delivery branch of pump including tapers, flanges,rubber gaskets,3mm thick as per BIS-2712-1978 nuts & bolts as per 1364-1983 & special up to 5 mtrs. Away from the outer wall of the pump house as per latout drawings approved by the Engineer-in-charge . The pipes shall be capable of with standing 1.5 times the total pressure indicated in item No.1e (II). |  |  |  | 1 |  |  |  | Each
Job
NOTE:- Actual laying to be done final dwawings to be approved by the Engineer in charge.
8 | Errection of all equipments from S.No. 1 to 4,6 & 7 including cost of tees, bends tapers & any other fittings required as per site conditions 7 as per direction of the Engineer-in-charge. |  |  |  | Job |  |  |  | Each
9 | Excavation in foundation trenches etc.(for pipes & pits up to all depths) in all kind of soil such as pick work, jumper work,blasting and chiselling soft or hard rock where blasing is prohibited in all leads and lifts including trimming and dressing of sides,levelling of bed to correct grade stacking the excavated soil clear from the edge of excavation and returning the excavated soil after laying, jointing and testing of MSERW pipes in trenches in 15 centimeters layers including consolidating each deposited layers by ramming and watering and then disposing of all surplus excavated soil as directed in all leads and lifts and soring strutting and timbering and dressing where ever required restoration of un-metalled/ metelled/ paved surface to its origenal condition including cost of diversion for traffic night signals, fixing caution boards, crossing over trenches for access to houses, fencing etc. complete in all respect and as per the direction of Engineer-in-Charge. |  |  |  | 96.04 |  |  |  | Per
[5 empty] | cubic |  |  |  | cubic
[5 empty] | metre |  |  |  | metre
10 | Laying, jointing and testing in trenches (to level or grade) of pipes jointed with every joint flanged confroming to IS 1239-1990 (Part-I) with lates upto date amendments of grade and wall thickness as specified below, suitable to withstand required bydraulic test pressure in randum length 4mm-6mm with plain ends and jointed with MS flanges conforming to IS 6392-1971 (latest upto date amendments) and welding of flanges as per IS 816-1969 with electrodes as per IS 814-1991 including required number and size of MS nuts and bolts as per IS 1369-1967 and compressed asbestos fibre jointing gaskets sheet not less than 3.00 mm in thickness as per IS 2712-1998. The welding of flanges to be done on both faces in two layers to make the joints leak proof and to entire satisfaction of the Engineer-in-Charge. The laying of pipes conform to IS 5822-1994 and as per CPHEEO manual and will include all operations such as cutting, welding and jointing including flushing, cleaning and hydraulic testing complete in all respect.
From To Length Class of pipe Wall Thickness Flange Table Dia of pipe
| 0 50 50 GMS(M) 4.00 17 100 mm dia |  |  |  | 50 |  |  |  | Per runningmetre
running
metre
| 50 260 210 GMS(M) 4.00 5 125 mm dia |  |  |  | 210 |  |  |  | Per runningmetre
running
metre
TERMS AND CONDITIONS (Puming Machinery)
1 | The firm shall forward a copy of supply order/indent placed by it for the supply of pumps and motors on the manufactures/ authorized dealers of the pumps and motors to the consignee within 30 days after the issue of the letter of intent/ award by the Engineer-in-Charge. The copy of the supply order/indent to the consignee should also accompany the dealership certificate of the dealer for the pumping machinery in case the pumps and motors are arranged from the authorized dealers.
2 | The firm shall arrange dispatch of offered pumps and motors to the consignee direct from the manufacturers/ their authorized dealers of the pumping machinery for which the supply order/indent has been placed by the firm. The packing slip should indicate the details of materials the package and material of construction of pumps and motors.
3 | The shop test for pumps and motors shall be carried out at manufactures works in the presence of representative of the department as per IS 325-1978. The test performance certificate of the pumping machinery shall be arranged by the firm fro the manufactures and get it approved from the Engineer-in-charge before actual dispatch of the pumping machinery.
4 | The firm shall supply the recommended list of spares and quantities required for normal working of the pumping machinery (Two years) from the manufactures of the aforesaid equipment at the time of quoting rates and shall quote items rate for the same also.
5 | The firm shall supply the manufacturer's manual for the operation and maintenance of the pumping equipment.
6 | The firm shall arrange operation and maintenance training to the operating staff for the pumping machinery (without extra cost ) for a period of seven days i.e. during the testing period.
7 | The characteristics curves of the pumping equipment shall be supplied with the offer, otherwise, the tender shall be rejected.
8 | The firm shall supply layout drawing in respect of various components, such as suction pipes, valves, cable trenches, control panel etc. from the foot valve location of the common header which shall extend up to 5 meters from the outer walls of the pump house towards rising main. The details of foundations required for various components shall also be supplied by the firm within 30 days of the letter of intent/ award.
9 | The installation of pumping machinery above 100 HP shall be inspected by the technical representative of the manufacturers, of rank not less than that of a service Engineer, at the work site and inspection certificate shall be supplied to the Engineer-in-charge. This inspection shall be in addition to the test report and nothing extra shall be paid on this account.
10 | All the civil works shall be constructed by the department.
11 | The wiring and installation of electric equipment shall be as per HPSEB rules and regulations and subjected to the approval of the Chief Electrical Inspector and or his authorized officer. Any defect pointed out shall be rectified by the firm without any extra cost. The wiring and installation of all electrical equipment shall be done by a licensed contractor of approved class of HPSEB authorities on their approved format (Form D) for release of power connection by the firm without extra cost.
12 | The temporary electric connection, if required during installation shall be arranged by the firm at its own cost and energy charges shall also be paid directly by the firm to the HPSEB.
13 | Prices of all items shall be F.O.R. site of work inclusive of all leads and shall be inclusive of all charges of transportation, insurance, packing, taxes and duties such as sales tax, excise duty and local taxes etc.
14 | The rates shall be quoted only on the format of schedule of quantities which is attached with the tender document giving all specified data so desired therein.
15 | The rates offered for the specified marks in the schedule of quantities only shall be considered. Rates quoted for the part or non specified marks shall lead to rejection of the tender.
16 | The location of site can be ascertained by the concerned Assistant Engineer & the rates quoted by the firm shall be inclusive of all mechanical and manual transport within all leads and lifts to the site of work.
17 | All the equipment/material shall confirm to the relevant BIS specifications wherever applicable and in its absence to any accepted National/International standards.
18 | The general specifications of the work shall conform to HP. PWD/Punjab PWD specifications as per direction to the Engineer-in-charge.
19 | The validity of the tender shall not be less than 120 days, otherwise, the tender shall be summarily rejected.
20 | All the equipment shall be guaranteed against any manufacturing defect including metallurgy and its performance for a period 12 (twelve) months from the date of commissioning/ 15 (fifteen) months from the date of supply which ever is earlier. Any defect if noticed within the stipulated period shall be rectified by the firm at its own cost with 15 days of bringing the same to its notice. The guarantee clause shall be substantiated by a guarantee bond of a nationalized bank for an amount equal to the cost of pumping and electrical equipment (accessories included) pledged in the name of the Executive Engineer in charge at the time of applying for refund of security deposits. The guarantee bond shall be released after the expiry of the guarantee period.
21 | The installed pumping machinery and other allied accessories shall be tested daily for stipulated pumping hours in the N.I.T. for a period of seven days without extra cost. However, the cost of electricity and water shall be borne by the department. During the guarantee period efficiency of the pumping and the electric equipment should not vary beyond the range of (+/-) 2.5%. If during guarantee period, the efficiency falls beyond 2.5% to a maximum of 5%, 1% cost of the pump set for 1% fall of the efficiency shall be deducted. In case of fall of efficiency beyond 5% the pump set shall be rejected and cost of the effected pump set recovered from the pledged bank guarantee and or from the security deposit as the case may be.
22 | 80% (Eighty percent) payment of the cost of pumping machinery and equipment less 10% security and other statutory recovery shall be made after receipt of complete pumping machinery i.e. pump and motors received together at site of work in good condition. The balance 20% cost after deduction of the security and other recoveries shall be released after successful and satisfactory installation, testing of the entire equipment. Ten percent security deposit shall be released as stipulated in the agreement.
23 | 90% (Ninety percent) installation charges shall be released after satisfactory installation of all the pumping and electrical equipment. Remaining 10 % of installation charges shall be released after testing of the entire equipment.
24 | In absence of performance curve, no offer will be entertained.
25 | The firm agreed to complete the work within 6 months.
26 | The firm agreed to supply a copy of order placed on the manufacturer to the divisional officer.
27 | The Executive Engineer will satisfy himself regarding model/make and characteristics of pump set before releasing any payment. The firm shall submita copy of test report along with supplies and Executive Engineer on scrutiny of test report only, shall release any payment.
28 | The pump set and all accessories shall carry a warrantee of 12 months from date of successful commissioning.
29 | The item of earthling includes all civil works required.
30 | The firm agreed to pay all taxes applicable including GST (Goods Service Tax) and nothing shall be claimed extra.
Rising main
1 | Conditional and telegraphic tenders are liable to be rejected.
2 | All pages of the tender form must be signed before submitting the tender failing which the tender is liable to be treated as in valid.
3 | The work will be executed as per HPPWD/HPIPH specifications, relevant IS codes and CPHEEO manual to the satisfaction of Engineer-in-charge.
4 | G.I. pipes will be issued free of cost to the contractor from Divisional store Differpat.
5 | The length of G.I. bends should not be less then 0.90 metre.
6 | The work should be carried out as per specifications.
7 | Nothing shall be paid for the rejected work/material.
8 | The work shall be completed with in stipulated period.
9 | Material should be ISI marked.
10 | The work should be executed as per recommendation of CPHEEO manual as water supply
11 | Statement of length where pipe is not buried under ground due to rocky strata shall be attached with every bill for the inspect of Engineer-in-Charge.
12 | 10% security, 2% Income Tax and 2% Sale tax will be deducted from each running bill of the contractor.
13 | All the necessary documents such as Income tax, clearance certificate, Sale tax No. and renewal of the registration should be shown to the undersigned at the time of purchase of schedule of quantity.
14 | Contractor will be held responsible for watch and ward of his material during execution.
15 | All the joints should be leak proof and final bill may not be released till the successful testing & running of the line.
16 | The quantity can be increased or decreased as per site conditions and contractor will have to execute the work at his quoted rate.
17 | Only those are allowed to purchase the tender documents who have best experience in for laying jointing of rising main and if required, undersigned can ask.
18 | All machineries equipments required for laying of pipe line will be arranged by contractor/firm other structure during the execution of work by the firm will be restored to original conditions.
19 | L-section/plan of the pipe line can be seen in the divisional officer at Palampur on any working day.
20 | The firm shall be make all the arrangement for working night hour (if required) at its own cost.
21 | Any damaged caused to metalled/macadam rod, street/path and to other structure during the execution of work by the firm will be restored to original condition.
22 | The rate of all item are inclusive of the carriage of all the material with in all leads and lifts to the site of work.
23 | The contractor shall be fully responsible for watch and ward of material at the site of work and in case of any theft or loss the recovery shall be made at the double cost of store issue rates.
24 | Royalty, sales tax,octrai etc. will be born by the contractor and proof there of shall have to be given without which no payment shall be done.
25 | Crushed stone aggregate shall be used at site of work.
26 | The contractor shall use vibrator/concreter mixer without any failure and in case of any inspection if it found that concreting is being done without vibrator the awarded rates in that particular item of work shall be reduced by 10%.
27 | The contractor agree to proved MSERW pipe 300 mm dia from the approved ISI manufacture.
28 | The firm agreed to pay all taxes applicable including GST (Goods Service Tax) and nothing shall be claimed extra.
29 | Cement will be issued @ Rs.275/-per bag from Divisional store Differpat.
30 | Steel will be issued @ Rs.4000/- per quintal to the contractor from Divisional store Differpat.
31 | Required No. of test cubes of cement concrete 1:5.5:3 from site shall be collected for random testing of their compressive strength at 28 days as per provision of BIS 456-2000 which shall be get tested from the lab of HPPWD of NIT Hamirpur.
TECHNICAL SPECIFICATIONS:-
1 | All pipe lines shall be tested in suitable sanctions after laying, The pressure shall not beless than 1-1/2 times the working pressure at the lowest point or the static head pressure which ever is higher. The procedure for test shall be in accordance with the clause 10.2 of IS 5822.
2 | BENDS
a) | Bends for pipes shall be fabricated from the parent tubes to be used in respective sections bends shall have three or more gussets with a bending radius of 5 time pipe dia to keep the frictional losses to bore minimum & should be factory made.
b) | All cut ends of the pipes shall be bevelled properly prior to welding operation.
3 | WELDING
a) | The electrodes to be used for welding shall conform to IS 814 and shall be overcereds type of advani overliken make.
b) | Seal welding shall be provided to all flanges with atleat to passes, using 3 mm electrodes.
4 | GASKETS
a) | Compressed asbestos fibre (CAF) 3 mm thick shall conform to 2712, Hindustan Farodom make and ISI marked or synthetic rubber, gaskets conform to BIS 838-1979 both lates with upto date amendments, suitable for working pressure of 25 Kg/Cm2.

## job3
SCHEDULE OF QUANTITY |  |  |  |  | Estimated Cost Rs. |  |  | 371250
C/O Lift Irrigation Scheme Mungal Ropa Gadiara in Tehsil Jaisinghpur Distt. Kangra (HP) |  |  |  |  | Earnest Money Rs. |  |  | 7425
Sub Head : Providing & errection of Pumping machinery with allied accessories for Ist and 2nd Phase) |  |  |  |  | Time :- |  |  | 6 Months
S. No. | Sub-Head and item of work |  |  | Quantity |  | Rate |  | Unit | Amount
[6 empty] | In Fig. | In words
Phase-I
1 | Providing of horigental spindle,horizontal/redial split casing/end suction(backpull out arrengement single/double/Multistage centrifugal pumps or combination of pumps in series/parallel of recommended make such as KSB/Mather & Platt/Kirloskar /Beaconweir/BE/Maxflow as per BIS 1520-1980 with upto date ammendments read with IS 9137-1978 or latest addition suitable for lifting water for under mentioned characteristics with bronze impellers/priming funnels: casingring and saftsleevs of bronze,saft of steel grade .... with cast iron casing coupled directly through a flexible coupling on a common CI/ cast steel base plate( base plate to be from manufacturer of the pumping unit only) to slip ring/squirrel cage screen protected drip proof induction motor/motors of standered make such as Kirlosker/ BHEL NGEF/ GEC/ Crompton/ Siemen/Joti/ABB and suitable for operation on 415(+/-) 5% volts 50 cycles/second,3 phase AC electric supply. The power of electric motor/motors should be at least+15% in excess of the maximum power required by the pump/pumps in the operation range of (+) 10% and (-) 15% of duty point head. The motor/motors as per IS:325-1978 with upto date ammendments raed with IS: 900-1972. It should include cost of bearing, nuts,bolts and painting etc. and should meet the following requirements:
|  |  |  | 2 set of |  |  |  | Per H.P.
15 HP
A) | SITE CONDITIONS
=
i) |  | Location of Site Palampur Jaisingh Pur Road Near Chadhiar
ii) |  | The altitude of place in which
the motor is intended to work
in ordinary service if it exceeds
1000 mt.
iii) |  | Humidity Weather generally remains humid during
monsoon season.
iv) |  | Nature of atmosphere As normally encounterd in Shivalik Range
v) |  | Detail of quality of water Clear cold water
vi) |  | Water free from sand or not Yes
vii) |  | Water corosive or not Not
viii) |  | Turbidity (if any) up to 500PPM
ix) |  | NPSH available Mts Postive suction
x) |  | Any other information or requirement
B) |  | OPERATING CONDITIONS
=
i) |  | Type of current AC three/single phase
ii) |  | Operating frequency 50 HZ
iii) |  | Rated voltage 400 (+/-) 10% volts
iv) |  | System of earthing if any to Double loop earthing as per BIS 3043-1987
to be adopted. latest with upto date ammendments
v) |  | No. of working hours per day 20.00 hours
vi) |  | Speed of revolution in RPM To be quoted by tenderer
vii) |  | Direction of rotation To be quoted by tenderer
viii) |  | The max. Temp. of cooling air 25 Degree Centigrade
& water in the place in which
the motor is intented to work
in ordinary service.
C) |  | MOTOR
= |  | ===========
i) |  | Ref to BIS code BIS 325-1978 read with BIS 900-1992
(latest)with upto date ammendments
ii) |  | Type of enclosure of motor SPDP(as per BIS 4691-1985 (latest)
iii) |  | Type of duty Continuous
iv) |  | Mechanical out put in KW Suitable for driving centrifugal pumps
required for duties specified against
pumps.To avoid overloading of motor a
margin of about 15-20% may be kept in
the rated out put of prime mover.
v) |  | Class of insulation Class ~B~/Class "F"
vi) |  | Max.permissible temp.rise of ---
motor reqd. if different from
given in B(viii) above
vii) |  | Particulars of test reqd. & As per terms & conditions
where they are to be conducted.
viii) |  | Particulars as to whether voltage ATS/star delta starter /Statar Rotor starter
limiting device will be employed oil immersed,fully automatic to
be installed between bus bar & motor.
Shunt capacitor is also proposed to be
installed for improving the power factor
at site.
NOTE:- Star delta starter upto 37.5 KW,
ATS between 37.5 KW to 50 KW & Stator rotor
starter with slip ring motor
ix) |  | Motor whether squirrel cage or Squirrel cage
slipring
x) |  | Details of shaft extension reqd. Just sufficient to provide direct drive
by flexible coupling to pump.
xi) |  | Type of slip ring gear whether Continouslly rated for Squirrel cage/
continouly rated or for starting Slipring motor
purposes only & whether to be fitted
with brush lifting or short circuiting
arrangements or both if interlocks
are rquired.
xii) |  | Breakway torque in terms of rated Breakway torque to be given by the tenderer
load torque & the corresponding but the starting current should not exceed
breakway starting current which 2.5 times of the full load current.
may be taken from the supply with
the starting apparatus in circuit.
xiii) |  | Nature of load & any information To work the pump offered
regarding the driven machine which
has a bearing upon the torque reqd.
during the accelerated period, the
kinetic energy of the moving parts
to be accelrated & No.of starts
during a specified period.
xiv) |  | Where possible fault capacity of The motor should be able to withstand
the system to which the motor is initial current of 2.5 times the rated
connected. current for two minutes without suffering
damages or permanent deformations.
D) |  | PUMP (BIS 1520-1980 ) read with BIS 9137-1978 both latest with up to date ammendments
a) |  | Nos of pumps reqd. 2 no. pumps
b) |  | Spare parts required For Two years normal maintenance as
recommended by manufacturer.
c) |  | Optional fittings reqd. Air cock for exahausting air from each
stage.
E) |  | PUMP OPERATING CONDITIONS
i) |  | Capacity 5.40 lps for each pump.
ii) |  | Total head in Mts. 112.14 mts
If total head is not known then
following details be provided:-
i) Static head 107 mts
ii) Minimum depth of water -- Postive suction
iii) Variation in water level -- mts
iv) Ground level to max. water level --- mts
v) Ground level to delivery point 694 mts
vi) Pressure in the suction tank ____ Kg/cm^2
vii) Pressure in the delivery tank ....... Kg/cm^2
iii) |  | Length of R/Main 350 mts
iv) |  | Dia of R/Main 150 mm
v) |  | Drive arrangement Direct through flexible coupling on a
common base plate/ suitable for reciprocating pump
vi) |  | Drive type Electric driven
vii) |  | NPSH reqd. To be quoted by the tenderer
viii) |  | Limits of total head in which (-) 15% to (+) 10% of total head.
the pump is reqd. to operate.
ix) |  | Suction/delivery size of pump To be specified by the tenderer
x) |  | Efficiency of pump at To be specified by the tenderer
a) duty head
b) (+)10 % head
c) (-)15 % head
xi) |  | Material of construction To be specified by the tenderer
(manufacturer~s certficate to be appended)
2 | Supply of suitable oil immersed star delta starterof standarad make such as |  |  | 2 |  |  | each
| MEI/Kilburn/Jyoti/ Siemens cnonforming to BIS-8544-1979 latest with up to date |  |  | Nos
ammendments for squirrel cage/slipriing motor (make to be specified by the tenderers)
mounted on panel board with magnetic type over load release & dashpot,time
lag,under voltage release with initial oil filling .
3 | Providing & fixing M S sheet 16 SWG steel fabricated floor mounted closed almirah type switch |  |  | 1 |  |  | Each
| board including angale iron post of suitable height and size ISA 40x40x6mm duly painted |  |  | No.
comprising and capable of mounting the following accessaries with all internal
electric connections. The drawing of panel board shall be subject to approval of
Engineer in charge.
a) | Ammeter of 60 Amp.AC supply,100 mm circular dial Auto electric/IMP/Havells make of suitable |  |  | 2 |  |  | Each
| range for above motor with selector switches conforming to BIS 1248-1983 latest with |  |  | No.
up to date ammendments.
b) | Voltmeter ( 0-500 volts)AC supply,100 mm circular dial Auto electric/AE/IMP/Havells make |  |  | 1 |  |  | Each
| of suitable range for above motor with selector switches conforming to BIS 4064-1978 |  |  | No.
with up to date ammendments.
c) | ICTP 63 Amp. switches with HRC fuses Kilburn/Larsen & turbo/Standard/Siemen make |  |  | 2 |  |  | Each
| and having capacity 30% extra of the operational rating of motor as per BIS 4064-1978 |  |  | Sets
with upto date ammendments immediatly after the power meter of HPSEB.
d) | Busbar chamber having 3 copper bars of suitable rating for full length equal to wirdth |  |  | 1 |  |  | Each
| of board of 3 live phases and one copper bar of half reating of full length for neutral |  |  | No
conforming to BIS 8084-1976 and 11353-1985 read with 5578-1985 all latest with upto
date ammendments.
e) | MCB of 63 Amp. capacity of Kilburn/LT/LK/MEI/Standard make on in comming feeder |  |  | 1 |  |  | Each
| for motors offered by the tenderer conforming to BIS 2516-1985 latest with upto date |  |  | No.
ammendments with neutral linked under voltage release.
f) | 3 phase indicating lamps complete with toggle switches for individual motors |  |  | 1 |  |  | Per set
| conforming to BIS 3452 part I & II latest with up to date ammendments. |  |  | Sets
g) | Earth leakage circuit breaker of requcemended (Kilburn/L&T/MET/GEC as per BIS-2516-1977 |  |  | 1 |  |  | Each
| with upto date ammendments and of suitaible range with which should have control box, |  |  | No.
oprating handel and trip/reset bush button on/ off indicators, re-indicating off spring condition
of the circut breaker for over current protection. The circuit should be equipped with magnet
thermal release with metallic tap CTS. It should also be fitted earth fault for tripping of breaker
on occurance of earth fault on/ of breaker load side.
h) | Hour run meter of reputed make of four digit capacity conforming to BIS-722(latest edition)/ |  |  | 2 |  |  | Each
| recommendations. |  |  | Nos.
i) | Suitable three phase voltage monitor relay with all protections & usual indicators with electrical |  |  | 1 |  |  | Each
| sirens against single phasing,no voltage,high voltage & overloading & phase voltage difference |  |  | No.
j) | Change over Switch of reputed make & suitable capacity |  |  | 1 |  |  | Each
No.
k) | Single phase preventor of reputed make & suitable capacity |  |  | 2 |  |  | Each
No.
4 (a) | Supply of Kirloskar/Kilburn/IVC/Fouress/Gled/BHEL/Leader/ Pelicon/KSB of reputed make
| of suitable size cast iron double flanged PN-1.6 sluice valve having size one step higer to |  |  | 2 |  |  | Each
| delivery of pump and capable of with standing nominal seat pressure of 16 kg/cm^2 |  |  | Nos
(b) | Supply of Kirloskar/Kilburn/IVC/Fouress/Gled/BHEL/Leader Pelicon/KSB of suitable size |  |  | 2 |  |  | Each
| cast iron PN-1.6 double flanged swing check type reflux valve having bye pass arrangement & |  |  | Nos
size one step higher to delivery of pump for withstanding nominal seat pressure of 16 kg/cm^2
(c) | Supply of Kirloskar/Kilburn/IVC/Fouress/Gled/BHEL/Leader/Pelicon/KSB of suitable size Cast |  |  | 1 |  |  | Each
| iron PN-1-6 double flanged swing check type reflux valve having bye pass arrangement & size |  |  | No.
equal to dia of R/main ie 100 mm diafor withstanding nominal seat pressure of 16 kg/cm^2
(d) | Supply of Kirloskar/Kilburn/IVC/Fouress/Gled/BHEL/Leader/Pelicon/KSB of reputed make of |  |  | 2 |  |  | Each
| suitable size cast iron double flanged sluice valve confirming IS 780, size equal to dia of suction pipe ; |  |  | Nos.
with hand wheel /cast iron cap and capable to with and knoing nominal sheet pressure of
16 kg/cm^2
5 (a) | P/L 6 sqmm copper PVC insulated armoured power 3 1/2 core cable conforming |  |  | 5 |  |  | Per Rmt
| to BIS 1554 (Part I) -1988 or latest with up to date ammendments Siemen/Gloster/ICC |  |  | Rmt
make from meter of HPSEB to OCB & from OCB to Busbar switch & starter (one cable
carrying all three phases) including all other electrical equipment/accessories such
as thimbles,flexible pipe,solder,nuts & bolts,cable glands etc. laid in pipes or
trenches under floor .The type,size & make will be subject to approval of HPSEB
authorities.In case of non acceptance by HPSEB authorities it shall have to be
replaced by the tenderer free of cost..
5(b) | P/L 4 sq. mm copper PVC insulated armoured power three core cable conforming |  |  | 5 |  |  | Per Rmt
| to BIS 1554(part I)-1988 or latest with up to date ammendments Siemen/Gloster/ICC |  |  | Rmt
make from switch to starter & starter to motor (one cable for carrying all three phases)
including all other electrical equipment /accesories such as thimbles,flexible pipes,
solder,nuts & bolts,cable glands etc. laid in pipes or trenches under floor.
The type,size & make will be subject to approval of HPSEB authorities.In case of non
acceptance by HPSEB authorities it shall have to be replaced by the tenderer free of cost.
5 (c) | P/L double loop earthing with copper plate 600x600x3mm thick electrode complete with |  |  | 1 |  |  | LS
| material such as charcoal, common salt ,GI pipes,thimbles,nuts & bolts,digging of pits,GI wiring |  |  | Job
& 25x5mm copper strips of required capacity conforming to BIS 3043-1987 latest with up to date
ammendments for above motors & other electrical equipment.
5 (d) | Supply & errection of floor/wall mounted power factor shunt capacitor conforming to BIS 2834- |  |  | 2 Nos |  |  | Each set or
| 1986 latest with upto date ammendments BHEL/GEC/Machneil/ Mager/Bajaj make to raise the |  |  | 2x4 KVAR |  |  | per KVAR
| prevailing power factor at site to 0.95 for direct connection to induction motor |  |  | =8KVAR
individually,of 2x 4 KVAR according to HP of motor offered including cable Siemens/
Gloster/ICC make from busbar chamber to capacitor & also including LT/LK/Kilburn
make ICTP switches conforming to BIS 4064-1978 or latest with HRC fuses (Range to be
specified by the tenderer.
6(a) | Supply of standarad make 100mm dia circular dial pressure gauge of suitable range Fiebeg/ |  |  | 2
| Bourden/ Precision make with all accessories such as stop cock,copper tubing etc. conforming |  |  | Nos |  |  | Each
to BIS 3624-1987 latest with up to date ammendments.
7 | Providing Laying suction,delivery pipe considering site requirements,NPSH required & available
& common header having area to two times the area of delivery branch of pump
including tapers,flanges,rubber gaskets,3mm thick as per BIS-2712-1978 nuts & bolts as per
1364-1983 & special up to 5 mtrs. away from the outer wall of pump house as per layout drawings
approved by Engineer-in-Charge The pipes shall be capable of withstanding 1.5 times the
total presure indicated in item no. 1e(ii).
|  |  | Suction pipe --------- mm dia | 5 | Rmt |  | Per Rmt
|  |  | Delivery pipe ---------mm dia | 5 | Rmt |  | Per Rmt
|  |  | Common header 150 mm dia | 8 | Rmt |  | Per Rmt
8 | Erection of all equipment including cost of tees,bends,tapes & any others |  |  | 1 |  |  | LS
| fittings required as per site conditions and as per direction of Engineer-in -Charge. |  |  | Job
2nd Phase
1 |  | Providing of horigental spindle,horizontal/redial split casing/end suction(backpull out arrengement single/double/Multistage centrifugal pumps or combination of pumps in series/parallel of recommended make such as KSB/Mather & Platt/Kirloskar /Beaconweir/BE/Maxflow as per BIS 1520-1980 with upto date ammendments read with IS 9137-1978 or latest addition suitable for lifting water for under mentioned characteristics with bronze impellers/priming funnels: casingring and saftsleevs of bronze,saft of steel grade .... with cast iron casing coupled directly through a flexible coupling on a common CI/ cast steel base plate( base plate to be from manufacturer of the pumping unit only) to slip ring/squirrel cage screen protected drip proof induction motor/motors of standered make such as Kirlosker/ BHEL NGEF/ GEC/ Crompton/ Siemen/Joti/ABB and suitable for operation on 415(+/-) 5% volts 50 cycles/second,3 phase AC electric supply. The power of electric motor/motors should be at least+15% in excess of the maximum power required by the pump/pumps in the operation range of (+) 10% and (-) 15% of duty point head. The motor/motors as per IS:325-1978 with upto date ammendments raed with IS: 900-1972. It should include cost of bearing, nuts,bolts and painting etc. and should meet the following requirements:
|  |  |  | 2 set of |  |  |  | Per HP
12.50 HP
A) |  | SITE CONDITIONS
=
i) |  | Location of Site Palampur Jaisingh Pur Road Near Chadhiar
ii) |  | The altitude of place in which
the motor is intended to work
in ordinary service if it exceeds
1000 mt.
iii) |  | Humidity Weather generally remains humid during
monsoon season.
iv) |  | Nature of atmosphere As normally encounterd in Shivalik Range
v) |  | Detail of quality of water Clear cold water
vi) |  | Water free from sand or not Yes
vii) |  | Water corosive or not Not
viii) |  | Turbidity (if any) up to 500PPM
ix) |  | NPSH available Mts Postive suction
x) |  | Any other information or requirement
B) |  | OPERATING CONDITIONS
=
i) |  | Type of current AC three/single phase
ii) |  | Operating frequency 50 HZ
iii) |  | Rated voltage 400 (+/-) 10% volts
iv) |  | System of earthing if any to Double loop earthing as per BIS 3043-1987
to be adopted. latest with upto date ammendments
v) |  | No. of working hours per day 20.00 hours
vi) |  | Speed of revolution in RPM To be quoted by tenderer
vii) |  | Direction of rotation To be quoted by tenderer
viii) |  | The max. Temp. of cooling air 25 Degree Centigrade
& water in the place in which
the motor is intented to work
in ordinary service.
C) |  | MOTOR
= |  | ===========
i) |  | Ref to BIS code BIS 325-1978 read with BIS 900-1992
(latest)with upto date ammendments
ii) |  | Type of enclosure of motor SPDP(as per BIS 4691-1985 (latest)
iii) |  | Type of duty Continuous
iv) |  | Mechanical out put in KW Suitable for driving centrifugal pumps
required for duties specified against
pumps.To avoid overloading of motor a
margin of about 15-20% may be kept in
the rated out put of prime mover.
v) |  | Class of insulation Class ~B~/Class "F"
vi) |  | Max.permissible temp.rise of ---
motor reqd. if different from
given in B(viii) above
vii) |  | Particulars of test reqd. & As per terms & conditions
where they are to be conducted.
viii) |  | Particulars as to whether voltage ATS/star delta starter /Statar Rotor starter
limiting device will be employed oil immersed,fully automatic to
be installed between bus bar & motor.
Shunt capacitor is also proposed to be
installed for improving the power factor
at site.
NOTE:- Star delta starter upto 37.5 KW,
ATS between 37.5 KW to 50 KW & Stator rotor
starter with slip ring motor
ix) |  | Motor whether squirrel cage or Squirrel cage
slipring
x) |  | Details of shaft extension reqd. Just sufficient to provide direct drive
by flexible coupling to pump.
xi) |  | Type of slip ring gear whether Continouslly rated for Squirrel cage/
continouly rated or for starting Slipring motor
purposes only & whether to be fitted
with brush lifting or short circuiting
arrangements or both if interlocks
are rquired.
xii) |  | Breakway torque in terms of rated Breakway torque to be given by the tenderer
load torque & the corresponding but the starting current should not exceed
breakway starting current which 2.5 times of the full load current.
may be taken from the supply with
the starting apparatus in circuit.
xiii) |  | Nature of load & any information To work the pump offered
regarding the driven machine which
has a bearing upon the torque reqd.
during the accelerated period, the
kinetic energy of the moving parts
to be accelrated & No.of starts
during a specified period.
xiv) |  | Where possible fault capacity of The motor should be able to withstand
the system to which the motor is initial current of 2.5 times the rated
connected. current for two minutes without suffering
damages or permanent deformations.
D) |  | PUMP (BIS 1520-1980 ) read with BIS 9137-1978 both latest with up to date ammendments
a) |  | Nos of pumps reqd. 2 no. pumps
b) |  | Spare parts required For Two years normal maintenance as
recommended by manufacturer.
c) |  | Optional fittings reqd. Air cock for exahausting air from each
stage.
E) |  | PUMP OPERATING CONDITIONS
i) |  | Capacity 3.91 lps for each pump.
ii) |  | Total head in Mts. 108.08 mts
If total head is not known then
following details be provided:-
i) Static head 103 mts
ii) Minimum depth of water -- Postive suction
iii) Variation in water level -- mts
iv) Ground level to max. water level 587 mts
v) Ground level to delivery point 690 mts
vi) Pressure in the suction tank ____ Kg/cm^2
vii) Pressure in the delivery tank ....... Kg/cm^2
iii) |  | Length of R/Main 250 mts
iv) |  | Dia of R/Main 125 mm
v) |  | Drive arrangement Direct through flexible coupling on a
common base plate/ suitable for reciprocating pump
vi) |  | Drive type Electric driven
vii) |  | NPSH reqd. To be quoted by the tenderer
viii) |  | Limits of total head in which (-) 15% to (+) 10% of total head.
the pump is reqd. to operate.
ix) |  | Suction/delivery size of pump To be specified by the tenderer
x) |  | Efficiency of pump at To be specified by the tenderer
a) duty head
b) (+)10 % head
c) (-)15 % head
xi) |  | Material of construction To be specified by the tenderer
(manufacturer~s certficate to be appended)
2 | Supply of suitable oil immersed star delta starter/stator rotor starter of standarad |  |  | 2 |  |  | each
| make such as MEI/Kilburn/Jyoti/ Siemens cnonforming to |  |  | Nos
BIS-8544-1979 latest with up to date ammendments for squirrel
cage/slipriing motor (make to be specified by the tenderers) mounted on panel board with
magnetic type over load release & dashpot,time lag,under voltage release with initial
oil filling .
3 | Providing & fixing M S sheet 16 SWG steel fabricated floor mounted closed almirah type switch |  |  | 1 |  |  | Each
| board including angale iron post of suitable height and size ISA 40x40x6mm duly painted |  |  | No.
comprising and capable of mounting the following accessaries with all internal
electric connections. The drawing of panel board shall be subject to approval of
Engineer in charge.
a) | Ammeter of 60 Amp. AC supply,100 mm circular dial Auto electric/AE/IMP/Havells make |  |  | 2 |  |  | Each
| of suitable range for above motor with selector switches conforming to BIS 1248-1983 |  |  | No.
latest withup to date ammendments.
b) | Voltmeter (0-500 volts) AC supply,100 mm circular dial Auto electric/AE/IMP/Havells |  |  | 1 |  |  | Each
| make of suitable range for above motor with selector switches conforming to |  |  | No.
BIS 4064-1978 with up to date ammendments.
c) | ICTP 63 Amp.switches with HRC fuses Kilburn/Larsen & turbo/Standard/Siemen |  |  | 2 |  |  | Each
| make and having capacity 30% extra of the operational rating of motor as per BIS 4064-1978 |  |  | Sets
with upto date ammendments immediatly after the power meter of HPSEB.
d) | Busbar chamber having 3 copper bars of suitable rating for full length equal to wirdth |  |  | 1 |  |  | Each
| of board of 3 live phases and one copper bar of half reating of full length for neutral |  |  | No
conforming to BIS 8084-1976 and 11353-1985 read with 5578-1985 all latest with upto
date ammendments.
e) | MCB 63 Amp. of suitable capacity of Kilburn/LT/LK/MEI/Standard make on in |  |  | 1 |  |  | Each
| comming feeder for motors offered by the tenderer conforming to BIS 2516-1985 latest |  |  | No.
with upto date ammendments with neutral linked under voltage release.
f) | 3 phase indicating lamps complete with toggle switches for individual motors |  |  | 1 |  |  | Per set
| conforming to BIS 3452 part I & II latest with up to date ammendments. |  |  | Sets
g) | Earth leakage circuit breaker of requcemended (Kilburn/L&T/MET/GEC as per BIS-2516-1977 |  |  | 1 |  |  | Each
| with upto date ammendments and of suitaible range with which should have control box, |  |  | No.
oprating handel and trip/reset bush button on/ off indicators, re-indicating off spring condition
of the circut breaker for over current protection. The circuit should be equipped with magnet
thermal release with metallic tap CTS. It should also be fitted earth fault for tripping of breaker
on occurance of earth fault on/ of breaker load side.
h) | Hour run meter of reputed make of four digit capacity conforming to BIS-722(latest edition)/ |  |  | 2 |  |  | Each
| recommendations. |  |  | Nos.
i) | Suitable three phase voltage monitor relay with all protections & usual indicators with electrical |  |  | 1 |  |  | Each
| sirens against single phasing,no voltage,high voltage & overloading & phase voltage difference |  |  | No.
j) | Change over Switch of reputed make & suitable capacity |  |  | 1 |  |  | Each
No.
k) | Single phase preventor of reputed make & suitable capacity |  |  | 2 |  |  | Each
No.
4 (a) | Supply of Kirloskar/Kilburn/IVC/Fouress/Gled/BHEL/Leader/ Pelicon/KSB of reputed make
| of suitable size cast iron double flanged PN-1-6 sluice valve having size one step higer to |  |  | 2 |  |  | Each
| delivery of pump and capable of with standing nominal seat pressure of 16 kg/cm^2 |  |  | Nos
(b) | Supply of Kirloskar/Kilburn/IVC/Fouress/Gled/BHEL/Leader Pelicon/KSB of suitable size |  |  | 2 |  |  | Each
| cast iron PN-1.6 double flanged swing check type reflux valve having bye pass arrangement & |  |  | Nos
size one step higher to delivery of pump for withstanding nominal seat pressure of 16 kg/cm^2
(c) | Supply of Kirloskar/Kilburn/IVC/Fouress/Gled/BHEL/Leader/Pelicon/KSB of suitable size Cast |  |  | 1 |  |  | Each
| iron PN-1.6 double flanged swing check type reflux valve having bye pass arrangement & size |  |  | No.
equal to dia of R/main ie 125 mm dia for withstanding nominal seat pressure of 16 kg/cm^2
(d) | Supply of Kirloskar/Kilburn/IVC/Fouress/Gled/BHEL/Leader/Pelicon/KSB of reputed make of |  |  | 2 |  |  | Each
| suitable size cast iron double flanged sluice valve confirming IS 780, size equal to dia of suction pipe ; |  |  | Nos.
with hand wheel /cast iron cap and capable to with and knoing nominal sheet pressure of
16 kg/cm^2
5 (a) | P/L 6 sq.mm copper PVC insulated armoured power 3 1/2 core cable conforming |  |  | 5 |  |  | Per Rmt
| to BIS 1554 (Part I) -1988 or latest with up to date ammendments Siemen/Gloster/ICC |  |  | Rmt
make from meter of HPSEB to OCB & from OCB to Busbar switch & starter (one cable
carrying all three phases) including all other electrical equipment/accessories such
as thimbles,flexible pipe,solder,nuts & bolts,cable glands etc. laid in pipes or
trenches under floor .The type,size & make will be subject to approval of HPSEB
authorities.In case of non acceptance by HPSEB authorities it shall have to be
replaced by the tenderer free of cost..
5(b) | P/L 4 sq.mm copper PVC insulated armoured power three core cable conforming |  |  | 5 |  |  | Per Rmt
| to BIS 1554(part I)-1988 or latest with up to date ammendments Siemen/Gloster/ICC |  |  | Rmt
make from switch to starter & starter to motor (one cable for carrying all three phases)
including all other electrical equipment /accesories such as thimbles,flexible pipes,
solder,nuts & bolts,cable glands etc. laid in pipes or trenches under floor.
The type,size & make will be subject to approval of HPSEB authorities.In case of non
acceptance by HPSEB authorities it shall have to be replaced by the tenderer free of cost.
5 (c) | P/L double loop earthing with copper plate 600x600x3mm thick electrode complete with |  |  | 1 |  |  | LS
| material such as charcoal, common salt ,GI pipes,thimbles,nuts & bolts,digging of pits,GI wiring |  |  | Job
& 25x5mm copper strips of required capacity conforming to BIS 3043-1987 latest with up to date
ammendments for above motors & other electrical equipment.
5 (d) | Supply & errection of floor/wall mounted power factor shunt capacitor conforming to BIS 2834- |  |  | 2 Nos |  |  | Each set or
| 1986 latest with upto date ammendments BHEL/GEC/Machneil/ Mager/Bajaj make to raise the |  |  | 2x4 KVAR |  |  | per KVAR
| prevailing power factor at site to 0.95 for direct connection to induction motor |  |  | =8KVAR
individually,of 2x4 KVAR according to HP of motor offered including cable Siemens/
Gloster/ICC make from busbar chamber to capacitor & also including LT/LK/Kilburn
make ICTP switches conforming to BIS 4064-1978 or latest with HRC fuses (Range to be
specified by the tenderer.
6(a) | Supply of standarad make 100mm dia circular dial pressure gauge of suitable range Fiebeg/ |  |  | 2
| Bourden/ Precision make with all accessories such as stop cock,copper tubing etc. conforming |  |  | Nos |  |  | Each
to BIS 3624-1987 latest with up to date ammendments.
7 | Providing Laying suction,delivery pipe considering site requirements,NPSH required & available |  |  | 1
| & common header having area to two times the area of delivery branch of pump |  |  | Job |  |  | L.S
including tapers,flanges,rubber gaskets,3mm thick as per BIS-2712-1978 nuts & bolts as per
1364-1983 & special up to 5 mtrs. away from the outer wall of pump house as per layout drawings
approved by Engineer-in-Charge The pipes shall be capable of withstanding 1.5 times the
total presure indicated in item no. 1e(ii).
|  |  | Suction pipe --------- mm dia | 5 | Rmt |  | Per Rmt
|  |  | Delivery pipe ---------mm dia | 5 | Rmt |  | Per Rmt
|  |  | Common header 150 mm dia | 8 | Rmt |  | Per Rmt
8 | Erection of all equipment including cost of tees,bends,tapes & any others |  |  | 1 |  |  | LS
| fittings required as per site conditions and as per direction of Engineer-in -Charge. |  |  | Job
Terms and conditions atteched
1 | The firm shall forward a copy of supply order/indent placed by it for the supply of pumps and motors on the manufactures/ authorized dealers of the pumps and motors to the consignee within 30 days after the issue of the letter of intent/ award by the Engineer-in-Charge. The copy of the supply order/indent to the consignee should also accompany the dealership certificate of the dealer for the pumping machinery in case the pumps and motors are arranged from the authorized dealers.
2 | The firm shall arrange dispatch of offered pumps and motors to the consignee direct from the manufacturers/ their authorized dealers of the pumping machinery for which the supply order/indent has been placed by the firm. The packing slip should indicate the details of materials the package and material of construction of pumps and motors.
3 | The shop test for pumps and motors shall be carried out at manufactures works in the presence of representative of the department as per IS 325-1978. The test performance certificate of the pumping machinery shall be arranged by the firm fro the manufactures and get it approved from the Engineer-in-charge before actual dispatch of the pumping machinery.
4 | The firm shall supply the recommended list of spares and quantities required for normal working of the pumping machinery (Two years) from the manufactures of the aforesaid equipment at the time of quoting rates and shall quote items rate for the same also.
5 | The firm shall supply the manufacturer's manual for the operation and maintenance of the pumping equipment.
6 | The firm shall arrange operation and maintenance training to the operating staff for the pumping machinery (without extra cost ) for a period of seven days i.e. during the testing period.
7 | The characteristics curves of the pumping equipment shall be supplied with the offer, otherwise, the tender shall be rejected.
8 | The firm shall supply layout drawing in respect of various components, such as suction pipes, valves, cable trenches, control panel etc. from the foot valve location of the common header which shall extend up to 5 meters from the outer walls of the pump house towards rising main. The details of foundations required for various components shall also be supplied by the firm within 30 days of the letter of intent/ award.
9 | The installation of pumping machinery above 100 HP shall be inspected by the technical representative of the manufacturers, of rank not less than that of a service Engineer, at the work site and inspection certificate shall be supplied to the Engineer-in-charge. This inspection shall be in addition to the test report and nothing extra shall be paid on this account.
10 | All the civil works shall be constructed by the department.
11 | The wiring and installation of electric equipment shall be as per HPSEB rules and regulations and subjected to the approval of the Chief Electrical Inspector and or his authorized officer. Any defect pointed out shall be rectified by the firm without any extra cost. The wiring and installation of all electrical equipment shall be done by a licensed contractor of approved class of HPSEB authorities on their approved format (Form D) for release of power connection by the firm without extra cost.
12 | The temporary electric connection, if required during installation shall be arranged by the firm at its own cost and energy charges shall also be paid directly by the firm to the HPSEB.
13 | Prices of all items shall be F.O.R. site of work inclusive of all leads and shall be inclusive of all charges of transportation, insurance, packing, taxes and duties such as sales tax, excise duty and local taxes etc.
14 | The rates shall be quoted only on the format of schedule of quantities which is attached with the tender document giving all specified data so desired therein.
15 | The rates offered for the specified marks in the schedule of quantities only shall be considered. Rates quoted for the part or non specified marks shall lead to rejection of the tender.
16 | The contractor is requestged to inspect the site before quoting his rate.
17 | All the equipment/material shall confirm to the relevant BIS specifications wherever applicable and in its absence to any accepted National/International standards.
18 | The general specifications of the work shall conform to HP. PWD/Punjab PWD specifications as per direction to the Engineer-in-charge.
19 | The validity of the tender shall not be less than 120 days, otherwise, the tender shall be summarily rejected.
20 | All the equipment shall be guaranteed against any manufacturing defect including metallurgy and its performance for a period 12 (twelve) months from the date of commissioning/ 15 (fifteen) months from the date of supply which ever is earlier. Any defect if noticed within the stipulated period shall be rectified by the firm at its own cost with 15 days of bringing the same to its notice. The guarantee clause shall be substantiated by a guarantee bond of a nationalized bank for an amount equal to the cost of pumping and electrical equipment (accessories included) pledged in the name of the Executive Engineer in charge at the time of applying for refund of security deposits. The guarantee bond shall be released after the expiry of the guarantee period.
21 | The installed pumping machinery and other allied accessories shall be tested daily for stipulated pumping hours in the N.I.T. for a period of seven days without extra cost. However, the cost of electricity and water shall be borne by the department. During the guarantee period efficiency of the pumping and the electric equipment should not vary beyond the range of (+/-) 2.5%. If during guarantee period, the efficiency falls beyond 2.5% to a maximum of 5%, 1% cost of the pump set for 1% fall of the efficiency shall be deducted. In case of fall of efficiency beyond 5% the pump set shall be rejected and cost of the effected pump set recovered from the pledged bank guarantee and or from the security deposit as the case may be.
22 | 80% (Eighty percent) payment of the cost of pumping machinery and equipment less 10% security and other statutory recovery shall be made after receipt of complete pumping machinery i.e. pump and motors received together at site of work in good condition. The balance 20% cost after deduction of the security and other recoveries shall be released after successful and satisfactory installation, testing of the entire equipment. Ten percent security deposit shall be released as stipulated in the agreement.
23 | 90% (Ninety percent) installation charges shall be released after satisfactory installation of all the pumping and electrical equipment. Remaining 10 % of installation charges shall be released after testing of the entire equipment.
24 | In absence of performance curve, no offer will be entertained.

## job 4
|  | * SCHEDULE OF QUANTITY * |  |  | Estimated cost:- | Rs. | 270452
| Name of work :- | Augmentation fo water supply scheme Shamlat Deh in Gram Panchayat Bandla in Tehsil Palampur District Kangra(HP). |  |  | Earnest money:- | Rs. | 5410
|  | (SH)Laying,jointing and testing of galvainsed iron pipe of following dia. |  |  | Time :- | Three months
Sr. | Description of items. |  | Qty. | Rate in |  |  | Unit | Amount
No. |  |  |  | Figures | Words
1 | Excavation in foundation trenches etc.in earth work in all kinds of soil such as pick work,jumper work,blasting in soft and hard rock and chiselling work including saturated soil slushy soil and under floor upto all depth and stacking the excavated soil not more than 3 metre clear from the edge of excavation and then returning the stacked soil in 15 centimetre (Fifteen centimetre)layer when required into plinth sides of foundation etc.consolidating each deposited layer by ramming and watering and then disposing of all surplus excavated earth as directed by the Engineer-in-charge within all leads and lifts. |  | 748.65 |  |  |  | Per
|  |  | cubic |  |  |  | cubic
|  |  | metre |  |  |  | metre
2 | Laying and jointing in trenches galvanised mild steel tubes,tube fitting (Light grade) of various dia. (Earth work in trenches to be measured and paid for separately) within all leads and lifts as per the direction of Engineer-in-charge.
| a) | 50 milimetre dia. | 1270 |  |  |  | Per
|  |  | running |  |  |  | running
|  |  | metre |  |  |  | metre
| b) | 40 milimetre dia. | 1830 |  |  |  | Per
|  |  | running |  |  |  | running
|  |  | metre |  |  |  | metre
Terms and conditions:-
a) | G.I.pipes will be issued free of cost to the contractor from Divisional store Differpat.
b) | Nothing shall be paid for the rejected work/material.
c) | The work should be carried out as per specifications.
d) | The work shall be completed with in stipulated period.
e) | Material should be ISI marked.
f) | The work should be executed as per recommendation of CPHEEO manual as water supply
g) | Statement of length where pipe is not buried under ground due to rocky strata shall be attached with every bill for the inspect of Engineer-in-Charge.